## MOP Template
Insert Supplier LOGO |  | Method of Procedure (MOP)
Project Title: XXXXX
Project Number: B3XXXXXX
Date:TBD |  |  |  | DUE 3 WEEKS BEFORE OUTAGE FOR REVIEW
Date | (approximate) Time | Additional PPE Required? (YES or N0) | Task # | TASK | Task Owner

## MOP Directions
Insert Supplier LOGO |  | Method of Procedure (MOP)
Project Title: XXXXX
Project Number: B3XXXXXX
Date:TBD
Date | (approximate) Time | Additional PPE Required? (YES or N0) | Task # | TASK | Task Owner
Tailboard (Tool box) discussion with all personnel associated with scheduled work
Identify date and timeline for each activity within the procedure. This will be utilized to track work progress against projected schedule
Identify SRP Critical Systems to be impacted. Record position of equipement being worked on to ensure proper alignment when work is complete, unless otherwise directed by SRP. (E.g. breaker position, valve position, etc.)
Identify necessary PPE; IE Arc Flash Protection, LOTO or COHE requirements are required
Identify each specific task required to be completed as part of the MOP, and resposible party for each individual task
Identify responsible party for each activity - contractor, SRP O&M, 3rd party supplier, etc…
Provide support documents from design that identify valve locations, piping demo/new install, panel schedules and impacted equipment, etc…
Reference SRP specification requirements and the associated specification sections for testing procedures; IE piping pressure test (221116-3.8B), chlorination process (221116-3.9C), Electrical Panelboard Testing (262416-3.2), HVAC Testing and Balancing (230593), etc…
Identify time for each contractor to complete their own QAQC exercise. Fill out all necessary forms 100% prior to inspections (E.g. voltage checks, rotation varifications, megger results, valve positions, etc.)
Identify time for work site clean up (housekeeping), tools and materials removed, etc… Is work area ready for occupancy?
Work complete, SRP contacted for inspections, support to bring critical systems back online, etc…

## Electrical Example
Insert Supplier LOGO |  | Method of Procedure (MOP)
Project Title: SRP POB Site Electrical Upgrades
Project Number: B3XXXXXX
Date:TBD
Date: | (approximate) Time | Additional PPE Required? (YES / N0) | Task # | TASK | Task Owner
TBD | 5:00 -5:15 am | N | 1 | Safety/Kick-off Meeting | Supplier
TBD | 5:00 -5:15 am | N |  | a. Job Safety, Scope | Supplier
TBD | 5:00 -5:15 am | N |  | b. Procedures L.O.T.O, PPE/Arc Flash, Mitagation plan /discussion of what could wrong, Shut off locations if emergency occurs. | Supplier
TBD | 5:15 -5:30 am | N | 2 | Verify with SRP ok to Power down panels HN3, LN3A, LN3B, HS3, LS3A, LS3B, LS3C | Supplier
TBD | 5:30 - 5:35 am | N | 3 | At SES open Fused Switch for panel HN3 and LOTO | SRP
TBD | 5:30 - 5:35 am | Y | 4 | At SES open Fused Switch for panel HS3 and LOTO | SRP
TBD | 5:35 - 5:45 am | N | 5 | At panel HN3 Verify Zero Voltage | Supplier
TBD | 5:45 - 5:50 am | N | 6 | At panel HS3 Verify Zero Voltage | Supplier
TBD | 5:50 - 5:55 am | Y | 7 | At North AC Unit Verify Zero Voltage | Supplier
TBD | 5:55 - 6:00 am | Y | 8 | At South AC Unit Verify Zero Voltage | Supplier
TBD | 6:00 - 10:00 am | Y | 9 | At the North AC & South AC remove the Disconnects & replace | Supplier
TBD | 10:00 - 2:00 pm | Y | 10 | Replace the wire from panels HN3 & HS3 | Supplier
TBD | 7:45 - 7:50 am | N | 11 | Connect new AC units - Megger / Record Results | Supplier
TBD | 7:50 - 7:55 am | Y | 12 | At SES remove LOTO & close Fused Switch to panel HN3 | SRP
TBD | 7:55 - 8:00 am | Y | 13 | At SES remove LOTO & close Fused Switch to panel HS3 | SRP
TBD | 8:00 am - 2:00 pm | N | 14 | At panel HN3 close breaker to North AC unit | Supplier
TBD | 8:00 am - 2:00 pm | N | 15 | At North AC Unit Verify Voltage & Rotation | Supplier
TBD | 2:00 - 2:15 pm | N | 16 | At panel HS3 close breaker to North AC unit | Supplier
TBD | 2:15 - 2:20 pm | N | 17 | At South AC Unit Verify Voltage & Rotation | Supplier

## Mechanical Example
Insert Supplier LOGO |  | Method of Procedure (MOP)
Project Title: EV01 Domestic Water Tie-in
Project Number: B3XXXXXX
Date:TBD
Date: | (approximate) Time | Additional PPE Required? (YES / N0) | Task # | TASK | Task Owner
2020-06-05 | 18:00 | No | 1 | Safety/Kick-off meeting | Supplier
|  | No | 2 | Tailboard meeting to discuss shutdown scope of work, shutdown timeline, critical tasks, mitigation plan /discussion of what could wrong, shut off locations if emergency occurs, etc… | Supplier
| 18:30 | Yes | 3 | Shutdown domestic water at Mechanical Room 13N7E | Supplier
| 19:00 | No | 4 | Drain water from pipe at mens restroom 8N5W | Supplier
| 23:00 | No | 5 | Cut and remove existing domestic water piping in (4) locations: | Supplier
Mechanical Room 13N2E
Custodial Room 10N5W
Northeast open office area 5N6E
Breakroom 1N3E
See attached Mech Piping drawing for piping demo's, shutoff valve location, new piping
2020-06-06 | 1:00 | Yes | 6 | Tie in new domestic water piping at (4) locations above | Supplier
| 5:00 | No | 7 | Solder and braze domestic water piping identified in line item #4 above | Supplier
| 7:00 | No | 8 | Pre-test domestic water piping for scheduled inspection, no water leaks | Supplier
Chlorination procedure to be completed on coordinated date (TBD)
| 8:00 | No | 9 |  | Supplier